## Sheet1
Location Summary
Montreal
Program
| ASHRAE 90.1-2004 Climate Zone | 5A
| Available Fuel Types | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame
| R-value (m2·K / W) | 2.1459
Roof
| Construction Type | IEAD
| R-value (m2·K / W) | 3.3784
Window
| U-Factor (W / m2·K) | 3.354
| SHGC | 0.385
| Visible transmittance | 0.305
Skylights/TDD
| U-Factor (W / m2·K) | n/a
| SHGC | n/a
| Visible transmittance | n/a
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_1_COOLC DXCOIL | 142.4152
| VAV_2_COOLC DXCOIL | 146.1537
| VAV_3_COOLC DXCOIL | 145.2154
Heating (kW)
| VAV_1_HEATC | 44.4857
| VAV_2_HEATC | 43.5081
| VAV_3_HEATC | 43.6039
HVAC Efficiency
Air Conditioning (COP)
| VAV_1_COOLC DXCOIL | 2.8
| VAV_2_COOLC DXCOIL | 2.8
| VAV_3_COOLC DXCOIL | 2.8
Heating Efficiency (%)
| VAV_1_HEATC | 0.8
| VAV_2_HEATC | 0.8
| VAV_3_HEATC | 0.8
HVAC Control - Economizer
| VAV_1_FAN | DifferentialDryBulb
| VAV_2_FAN | DifferentialDryBulb
| VAV_3_FAN | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 6.9
| VAV_2_FAN | 7.54
| VAV_3_FAN | 7.47
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.088041
| Total Cost ($/m2) | 17.01
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.0083025
| Total Cost ($/m2) | 0.44
Total Utility Costs
| Cost Intensity ($/m2) | 17.45
Energy - End Uses
Electricity (kWh)
| Heating | 215697.2222
| Cooling | 86750
| Interior Lighting | 264338.8889
| Exterior Lighting | 77716.6667
| Interior Equipment | 296255.5556
| Exterior Equipment | 0
| Fans | 21491.6667
| Pumps | 75
| Heat Rejection | 0
| Humidification | 0
| Heat Recovery | 0
| Water Systems | 0
| Refrigeration | 0
| Generators | 0
| Total End Uses | 962325
Gas (MJ)
| Heating | 227890
| Cooling | 0
| Interior Lighting | 0
| Exterior Lighting | 0
| Interior Equipment | 0
| Exterior Equipment | 0
| Fans | 0
| Pumps | 0
| Heat Rejection | 0
| Humidification | 0
| Heat Recovery | 0
| Water Systems | 36970
| Refrigeration | 0
| Generators | 0
| Total End Uses | 264860
Purchased Cooling (MJ)
| Heating | 0
| Cooling | 0
| Interior Lighting | 0
| Exterior Lighting | 0
| Interior Equipment | 0
| Exterior Equipment | 0
| Fans | 0
| Pumps | 0
| Heat Rejection | 0
| Humidification | 0
| Heat Recovery | 0
| Water Systems | 0
| Refrigeration | 0
| Generators | 0
| Total End Uses | 0
Purchased Heating (MJ)
| Heating | 0
| Cooling | 0
| Interior Lighting | 0
| Exterior Lighting | 0
| Interior Equipment | 0
| Exterior Equipment | 0
| Fans | 0
| Pumps | 0
| Heat Rejection | 0
| Humidification | 0
| Heat Recovery | 0
| Water Systems | 0
| Refrigeration | 0
| Generators | 0
| Total End Uses | 0
| Total Building (MJ) | 3729220
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 155.8572
| Cooling (elec) | 62.6833
| Interior Lighting (elec) | 191.0044
| Exterior Lighting (elec) | 56.156
| Interior Equipment (elec) | 214.0665
| Exterior Equipment (elec) | 0
| Fans (elec) | 15.5293
| Pumps (elec) | 0.054193
| Heat Rejection (elec) | 0
| Humidification (elec) | 0
| Heat Recovery (elec) | 0
| Water Systems (elec) | 0
| Refrigeration (elec) | 0
| Generators (elec) | 0
| Total End Uses | 695.3508
Gas (MJ/m2)
| Heating (gas) | 45.7409
| Cooling (gas) | 0
| Interior Lighting (gas) | 0
| Exterior Lighting (gas) | 0
| Interior Equipment (gas) | 0
| Exterior Equipment (gas) | 0
| Fans (gas) | 0
| Pumps (gas) | 0
| Heat Rejection (gas) | 0
| Humidification (gas) | 0
| Heat Recovery (gas) | 0
| Water Systems (gas) | 7.4204
| Refrigeration (gas) | 0
| Generators (gas) | 0
| Total End Uses | 53.1614
Purchased Cooling (MJ/m2)
| Heating | 0
| Cooling | 0
| Interior Lighting | 0
| Exterior Lighting | 0
| Interior Equipment | 0
| Exterior Equipment | 0
| Fans | 0
| Pumps | 0
| Heat Rejection | 0
| Humidification | 0
| Heat Recovery | 0
| Water Systems | 0
| Refrigeration | 0
| Generators | 0
| Total End Uses | 0
Purchased Heating (MJ/m2)
| Heating | 0
| Cooling | 0
| Interior Lighting | 0
| Exterior Lighting | 0
| Interior Equipment | 0
| Exterior Equipment | 0
| Fans | 0
| Pumps | 0
| Heat Rejection | 0
| Humidification | 0
| Heat Recovery | 0
| Water Systems | 0
| Refrigeration | 0
| Generators | 0
| Total End Uses | 0
| Total Building (MJ/m2) | 748.5102
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 361.1802
| Feb | 310.476
| Mar | 291.3385
| Apr | 281.8583
| May | 216.1214
| Jun | 257.6405
| Jul | 263.7121
| Aug | 260.9485
| Sep | 218.9209
| Oct | 264.29
| Nov | 293.5211
| Dec | 332.5695
Time of Peak Electrical Demand
| Jan | 02-JAN-08:09
| Feb | 06-FEB-08:09
| Mar | 20-MAR-05:10
| Apr | 03-APR-05:10
| May | 01-MAY-05:10
| Jun | 08-JUN-12:00
| Jul | 13-JUL-15:09
| Aug | 04-AUG-15:50
| Sep | 06-SEP-15:09
| Oct | 02-OCT-05:10
| Nov | 20-NOV-06:10
| Dec | 26-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 12573.86
| Total Source Energy (MJ/m2) | 2523.76
Water Consumption (m3)
| Cooling | 0
| Heat Rejection | 0
| Water Systems | 174.59
| Total Building | 174.59
Emissions
| Carbon Equivalent (kg) | 517838.333
| CO2 (kg) | 1197570
| NOX (kg) | 2168.0562
| SO2 (kg) | 6485.3642
| PM (kg) | 0
| Hg (kg) | 0.0196
| Water for Electricity (m3) | 1492.99